## Slide 1: Emergency Preparedness During Decommissioning
David Daigle
Project Manager/Emergency Preparedness Specialist
Fall 2016 Low-Level Radioactive Waste Forum
Saratoga Springs, New York
November 7, 2016

## Slide 2: Overview of the EP Transition
Previous Licensing Actions
Transition process has evolved to include:
  Post-Shutdown License Amendment Request (LAR)
  Permanently Defueled LAR
  Regulatory Exemption Request (Based on precedent from above plants)
  ISFSI-Only Emergency Plan LAR
Humboldt Bay – 7/2/1976 | Trojan – 11/2/1992
La Crosse – 4/30/1987 | Haddam Neck – 7/22/1996
Rancho Seco – 6/7/1989 | Maine Yankee – 12/6/1996
Fort St. Vrain – 8/18/1989 | Zion – 2/21/1997
Yankee Rowe – 10/1/1991 | Big Rock Point – 8/29/1997

## Slide 3: Recent and Announced Shutdowns
2013
  Kewaunee / Crystal River Unit 3 / San Onofre Units 2 & 3
2014
  Vermont Yankee
2016
  Fort Calhoun
2017
  FitzPatrick / Clinton
2018
  Quad Cities Units 1 & 2
2019
  Pilgrim / Oyster Creek
2024-2025
  Diablo Canyon Units 1 & 2

## Slide 4: Decommissioning Emergency Plans
Objective
  Continue to maintain public health and safety
While also…
  Maximizing use of decommissioning funds
  How are these objectives met?
  The scope of the Emergency Plan is commensurate with the radiological risk at each phase of the transition

## Slide 5: Example Staffing Reductions
Chart: 
| Shutdown | + 1 Month | + 18 Months
 | 650 | 450 | 320 | 300 | 295 | 290 | 285 | 280 | 275 | 270 | 265 | 260 | 255 | 250 | 245 | 240 | 235 | 230 | 230 | 180 | 170 | 160

## Slide 6: Difficulties
Emergency Planning regulations do not distinguish between an operating plant and a permanently shutdown plant
Over 15 years since last plant shutdown
Absence of existing guidance
Regulatory exemption criteria
September 11 and Fukushima
Stewardship of the decommissioning trust fund

## Slide 7: Emergency Plan Transition
IOEP
All Fuel in ISFSI
Zirc Fire Milestone
PDEP*
PSEP
Post-Shutdown
Emergency Plan
Permanently Defueled
Emergency Plan
ISFSI-Only Emergency Plan
Reactor Permanently Defueled
Approximately 16 - 18 Months
Fuel Transfer to ISFSI
* Implementation of the PDEP is based on NRC approval of Regulatory Exemption requests.

## Slide 8: Post-Shutdown Emergency Plan
Continue to meet regulatory requirements for an operating plant
On-shift staffing changes
Emergency Response Organization staffing (ERO) changes
Evaluation of potential impact on Offsite Response Organizations (OROs)
Emergency Action Level (EAL) changes can be addressed in this submittal or in a separate request
Notes: On-Shift Staffing Changes
Staffing is reduced from normal operating levels to levels needed to safely store spent fuel at the facility
Primary justification is provided by an on-shift staffing analysis
  Able to cope with the spectrum of remaining credible events
  B.5.b/10 CFR 50.54(hh)(2) SFP inventory makeup strategies are required until all spent fuel is transferred to dry storage
On-shift staff typically consists of 3 personnel:
  Shift Manager
  Non-Certified Operator
  Radiation Protection Technician
  ERO Shift Staffing Changes
ERO Task Analysis
  Is a specific task still required?
  Is the position performing a required task being eliminated?
  If so, which remaining position will perform the task?
ERO typically consists of two (2) augmented responders within two (2) hours of an Alert
  Technical Coordinator
  Radiation Protection Coordinator
  Impact on ORO
Objective evidence that proposed changes will not impact the licensee’s ability to interface with State and local officials or impact the ability of the State and local agencies to implement their emergency plans
Documentation of discussions with State and local officials
  Not concurrence unless the proposed changes impact the offsite REP plans
If REP plans are impacted, then FEMA review is needed
  EAL Changes
Licensees will continue to use a standard EAL scheme
Their operating plant EAL current scheme will be modified to reflect the permanently defueled condition
Changes would be limited to those that reflect:
  Operating Modes that are no longer applicable
  Plant Conditions that are no longer applicable
  Equipment that is no longer required

## Slide 9: Pre-Implementation Drill
OROs should be provided the opportunity to participate in the validation drills
NRC and FEMA provided an opportunity to observe

## Slide 10: Regulatory Exemptions
From 10 CFR 50.47 and Appendix E
NSIR/DPR-ISG-02, “Emergency Planning Exemption Requests for Decommissioning Nuclear Power Plants”
Traditional accidents that dominate operating plant risk are no longer applicable
  Risk to public is primarily associated with the spent fuel stored in the Spent Fuel Pool (SFP)
  Risk of a SFP accident is lower than accident risk in an operating plant
Accident Analyses
Notes: ISG-02 Provides guidance to NRC staff on requests for exemptions and review of changes to the Emergency Plan reflecting the exemptions, as granted
    SFP at atmospheric pressure
    Fuel is subcritical
    Heat source is low
Emergency Planning regulations do not distinguish between an operating plant and a permanently shutdown plant
Accident Analyses
Remaining Applicable Design Basis Accidents
  Typically a Fuel Handling Accident in the SFP
Adiabatic Heat Up Analysis
  >10 hours is available before any fuel cladding temperature reaches 900oC from the time all cooling is lost
Loss of SFP Water Inventory
  Results in radiation exposure at the Exclusion Area Boundary and Control Room
Site-Specific Seismic Hazard Assessment
  Evaluation demonstrating a high confidence of a low probability of seismic failure of the SFP, or
  Analysis demonstrating natural air flow is sufficient in a completely drained pool to maintain peak cladding temperature below 565 degrees Celsius

## Slide 11: Permanently Defueled Emergency Plan
Operating Reactor(s) | Decommissioning Site
Focused on response to a variety of emergencies related to an operating reactor | Focused on SFP events (permanently shutdown/defueled reactor)
Formal offsite REP plans Emergency Planning Zone Alert and Notification System | Comprehensive (all hazards) planning Coordination with firefighting, medical, law enforcement responding onsite
Event Classification Unusual Event, Alert, Site Area Emergency, General Emergency | Event Classification Unusual Event, Alert
Notification of Event Declaration 15 minutes (State and local) | Notification of Event Declaration Prompt (designated agencies)
Dedicated on-and offsite facilities | Onsite “Command Center”
Joint, biennial exercises | Onsite biennial exercise OROs invited to participate
Notes: Implements exemptions, as approved by the NRC
No additional analyses is needed to support the PDEP beyond what would be provided to the NRC in the EP Exemption Request
  Elimination of EPZs
  No prompt alert and notification system
  No evacuation time estimates
  No periodic public information
  No potassium iodide
  No offsite pre-planned protective actions
  No 15 minute notification time requirement
  Emergency Classifications
  Limited to Unusual Event and Alert
  No 15 minute classification time requirement
  Elimination of Emergency Response Facilities
  No Emergency Operations facility
  No Technical Support Center
  No Operational Support Center
  No alternate facilities
  Emergency Exercises
  No offsite participation biennial exercise
  No submittal of exercise scenarios
  No 8-year exercise cycle requirements
  No wide-spectrum of events including hostile action requirement
  Hostile Action Requirements
  No alternate facility
  No hostile action exercise
  No onsite protective actions for hostile action
  Some EP requirements for security-based events are maintained
    Security EALs are maintained
    Licensees are required to maintain the SFP mitigation strategies

## Slide 12: ISFSI-Only Emergency Plan
Continues to meet regulatory requirements, as previously exempted
  Requirements similar to those required by Part 72.32(a)
  No additional exemptions are required
Emergency Plan address the permanent removal of fuel from the SFP to dry cask storage
  Changes to on-shift and ERO staffing
  EALs for ISFSI only
Notes: Staffing Changes
Reduced from normal operating conditions to levels commensurate with the need to store spent fuel
On-Shift Staffing is typically reduced to an ISFSI Shift Supervisor (ISS)
ERO typically consists of:
  1. Resource Manager
    In contact with ISS/Emergency Director within two (2) hours of an Alert declaration
    Assists in assessing the emergency condition and coordinating resources
    Response can be accomplished remotely
  2. Individual trained in radiological monitoring and assessment
    Reports to ISFSI within four (4) hours of an emergency declaration for an event involving radiological consequences
EAL Changes
Eliminate EALs associated with:
  SFP operation
  Radiological effluents not associated with the ISFSI
    Administrative controls would be established during dismantlement activities
  Security conditions associated with aircraft

## Slide 13: Summary
Transition Consists of:
  Post-Shutdown Emergency Plan
  Permanently Defueled Emergency Plan
    Based on NRC-approved regulatory exemptions
  ISFSI-Only Emergency Plan

## Slide 14: Questions
David Daigle
Project Manager/
Emergency Preparedness Specialist
(813) 962-1800 ext. 602
ddaigle@enercon.com